## Q4-Q5 Module and Roof
Q4/Q5 – PV Module Selection & Roof Layout ¦ Tampa 5m×18m ¦ 35° Tilt
A. Module Selection – AIKO Neostar 490W chosen over LonGi Hi-MO X6 600W
Parameter | AIKO 490W (SELECTED) | LonGi 600W | Decision reason
Pmax (STC) | 490 W | 600 W
Module efficiency | 24.5% | 23.2% | AIKO higher efficiency
Dimensions (L×W) | 1762×1134 mm | 2278×1134 mm | LonGi too long for roof – see below
Temp coeff Pmax | -0.26%/°C | -0.29%/°C | AIKO better in Florida heat
Annual degradation | ≤0.35%/yr | 0.40%/yr | AIKO degrades slower
Voc (STC) | 41.10 V | 52.81 V
Vmp (STC) | 34.70 V | 44.66 V
Isc (STC) | 14.88 A | 14.46 A
Imp (STC) | 14.13 A | 13.44 A
Max sys voltage | DC 1500V | DC 1500V
Fire rating | IEC Class A | UL Type 1/2
Product warranty | 25 yr | 15 yr | AIKO longer warranty
FITS ROOF (portrait)? | ✓ YES – 1.762m < 2.052m | ✗ NO – 2.278m > 2.052m | LonGi eliminated here
B. Roof Geometry & Available Area
Parameter | Calculation | Result
Total roof width | Given | 5.0 m
Total roof length | Given | 18.0 m
Tilt angle | Given | 35°
Horizontal half-width per slope | 5.0 ÷ 2 | 2.5 m
Slope surface width | 2.5 ÷ cos(35°) | 3.052 m
Safety margin each side | Assignment requirement | 0.5 m
Available along slope | 3.052 − 2×0.5 | 2.052 m
Available along ridge | 18.0 − 2×0.5 | 17.0 m
C. Cluster Layout Calculation
Parameter | Calculation | Result | Notes
Module orientation | Portrait chosen | 1.762m along slope, 1.134m along ridge
Rows per cluster | floor(2.052 ÷ 1.762) | 1 row | 1.762m < 2.052m available ✓
Cols per cluster | Max allowed | 4 columns
Cluster width (ridge) | 4 × 1.134m | 4.536 m
Inter-cluster gap | Assignment requirement | 0.5 m
Clusters that fit | floor((17+0.5) ÷ (4.536+0.5)) | 3 clusters
Ridge length occupied | 3×4×1.134 + 2×0.5 | 14.608 m | < 17.0m ✓
Modules per slope | 1 row × 3 clusters × 4 cols | 12 modules
Total modules (2 slopes) | 12 × 2 | 24 modules | 12 south + 12 north
TOTAL INSTALLED kWp | 24 × 490W | 11.76 kWp

## Q4-Q7 Inverter and CC
Q4/Q7 – Inverter & Charge Controller Selection ¦ 120V/60Hz ¦ Tampa
A. Inverter Selection – UL Variants Only (120V/60Hz North America)
Parameter | SW 4024 | SW 4048 | XW Pro 6848 | Notes
Cont. output power (25°C) | 3,400 W | 3,800 W | 6,800 W | Critical load = 6,000 W
DC bus voltage | 24 V | 48 V | 48 V
Output voltage | 120/240 V | 120/240 V | 120/240 V split-phase
Output frequency | 60 Hz | 60 Hz | 60 Hz
Li-ion compatible? | ✗ No | ✗ No | ✓ Yes | Required for LFP bank
Peak efficiency | 92% | 94% | 96.1%
CEC weighted eff. | – | – | 94.1% | Used for GT calculations
Transfer time | <16.7 ms | <16.7 ms | 8 ms | Faster for data center
Covers 6 kW load? | ✗ NO | ✗ NO | ✓ YES | SW units eliminated
B. Inverter Voltage Clarification – IMPORTANT
The XW Pro 6848 NA is used in the 120/240V split-phase configuration. Tampa requires 120V/60Hz (Table I), which is standard North American split-phase service. The 6,800W continuous rating applies to this split-phase configuration and covers the 6,000W critical load. In 120V-only single-phase mode the rating drops to 5,760W, which would be insufficient. A North American data-centre switchboard provides 120/240V split-phase — this is the assumed installation configuration.
C. String Configuration for CC Selection
Parameter | Value | Unit | Formula | Notes
Modules per slope | 12
String config | 6S × 2P |  | per CC | Two strings of 6 in series
Voc per CC (STC) |  |  | V
Vmp per CC (STC) |  |  | V
Isc per CC (STC) |  |  | A
Imp per CC (STC) |  |  | A
Power per CC |  |  | W
Voc at cold (-5°C Tampa low) |  | ≈ 262.9 | V
D. Charge Controller Comparison
Check | MPPT 60-150 | MPPT 80-600 | MPPT 100-600 | Limit values
Max PV Voc limit | 150 V | 600 V | 600 V
Max array Isc | 60 A | 28 A | 35 A
Max output power (48V) | 3,500 W | 4,800 W | 6,000 W
Max charge current | 60 A | 80 A | 100 A
MPPT voltage range | Batt+5–140 V | 195–510 V | 195–510 V
Efficiency (48V nominal) | 98% | 95% | 95%
Array: Voc=246.6V ¦ Vmp=208.2V ¦ Isc=29.76A ¦ Power=5,880W
Voc 246.6V ≤ limit? | ✗ FAIL (>150V) | ✓ PASS | ✓ PASS | Limit: 150 / 600 / 600V
Vmp 208.2V in range? | ✗ FAIL | ✓ PASS | ✓ PASS | Range: –/195-510/195-510V
Isc 29.76A ≤ limit? | ✓ PASS (29.76<60) | ✗ FAIL (29.76>28) | ✓ PASS (29.76<35) | Limit: 60/28/35A
Power 5880W ≤ limit? | ✗ FAIL (>3500W) | ✗ FAIL (5880>4800) | ✓ PASS (5880<6000) | Limit: 3500/4800/6000W
ALL PASS? | ✗ NO | ✗ NO | ✓ YES
SELECTED: 2 × Conext MPPT 100-600 (one per slope) ¦ Part 865-1034 ¦ 95% efficiency

## Q8 Battery Bank Design
Q8 – Final Battery Bank Design ¦ 4S×5P ¦ 20 × Victron LFP 12.8V/330Ah
A. DC Energy Requirement (includes inverter losses)
Parameter | Formula / Value | Result | Notes
Critical AC load | Given | 6.0 kW | Load 3
Blackout duration | 20:00 Thu → 04:00 Fri | 8 h
AC energy per event |  | 48.0 kWh
Blackout inverter efficiency | From efficiency curve @ 88.8% | 91.3931%
DC ENERGY NEEDED PER EVENT |  | 52.520 kWh | Battery must supply this DC energy
Max DoD constraint | Assignment: max 80% DoD | 80%
Min nominal capacity required |  | 65.650 kWh
B. Bank Configuration
Parameter | Formula / Value | Result | Notes
Battery type | Victron LFP Smart | 12.8V / 330Ah | Integrated BMS, 2500 cycles @ 80% DoD
Energy per unit |  | 4.224 kWh
DC bus voltage (inverter) | XW Pro 6848 requirement | 48V nominal
Series units per string |  | 4S → 51.2V
String capacity (Ah) | Series: same Ah | 330 Ah | Series connection keeps Ah unchanged
String energy |  | 16.896 kWh
Parallel strings | ceil(65.65 / 16.896) | 4P would give 67.58kWh; 5P selected for margin
TOTAL BATTERIES |  | 20 batteries | Within 20-unit BMS limit ✓
Bank voltage |  | 51.2 V
Bank total Ah |  | 1,650 Ah
NOMINAL CAPACITY |  | 84.48 kWh
C. Usable Capacity & Margin (both DoD interpretations presented)
The assignment states max DoD = 80% and charging ceiling = 95% SoC. There are two defensible interpretations of how the DoD floor is calculated: • Interpretation A (DoD from starting SoC 95%): floor = 95% − 80% = 15% SoC → usable = 80% × 84.48 = 67.58 kWh → margin = 15.06 kWh • Interpretation B (DoD from full charge 100%): floor = 100% − 80% = 20% SoC → usable = 75% × 84.48 = 63.36 kWh → margin = 10.84 kWh Both interpretations pass. Actual minimum SoC reached in simulation: 32.8% — well above both floors. The design is robust under either interpretation.
D. 3-Year Degradation Check
Parameter | Representative Year 1 | Representative Year 2 | Representative Year 3 + end
Cumulative cycles | 52 | 104 | 156
Nominal capacity (kWh) | 84.480 | 83.601 | 82.723
Degradation (%) | 0.000% | 1.040% | 2.080%
Usable – Interp A (80%×nom) | 67.584 | 66.881 | 66.178
Usable – Interp B (75%×nom) | 63.360 | 62.701 | 62.042
DC demand per event (kWh) | 52.520 | 52.520 | 52.520
Margin A (kWh) | 15.064 | 14.361 | 13.658
Margin B (kWh) | 10.840 | 10.181 | 9.522
All blackouts covered? | ✓ YES – both interpretations | ✓ YES – both interpretations | ✓ YES – both interpretations

## Q6 Inverter Efficiency
Q6 – Inverter Efficiency Analysis ¦ XW Pro 6848 NA
A. Key Operating Points
Mode | Load % | Efficiency | Notes
GT – low irradiance | 5.0% | 86.41%
GT – morning/evening | 10.0% | 92.24%
GT – moderate | 25.0% | 94.77%
GT – PEAK EFFICIENCY | 27.5% | 94.80% | Max efficiency point
GT – strong sun | 50.0% | 93.99%
GT – near max PV | 80.0% | 92.03%
BLACKOUT fixed load | 88.8% | 91.39% | Fixed point all blackouts
Full rated output | 100.0% | 90.56%
B. Grid-Tied vs Blackout Comparison
Parameter | Value | Unit | Notes
Grid-tied weighted avg (Year 1) | 92.36% |  | Weighted by AC output over all GT hours
Blackout fixed efficiency | 91.39% |  | At 88.8% of PDC0
Peak efficiency | 94.80% |  | At 27.5% load
Difference (GT − blackout) | 0.96 | pp
C. Explanation
GRID-TIED (avg 92.4%): PV operates at variable power. Tampa's solar distribution means the array frequently runs at 10–50% of rated output, near the peak-efficiency region. Output-weighted average efficiency is therefore close to the partial-load optimum. BLACKOUT (fixed 91.4%): The inverter always supplies exactly 6 kW — 88.8% of rated output. Above the ~27.5% peak-efficiency point, I²R losses in switches and magnetics rise quadratically with current, reducing efficiency. This is why 88.8% load gives LOWER efficiency than the grid-tied weighted average, which includes many lighter-load hours.

## Q9 Currents
Q9 – Charging & Discharging Currents ¦ 4S×5P ¦ 51.2V / 1,650Ah
A. Maximum Discharge Current
Parameter | Formula | Result | Notes
DC bus voltage | 4 × 12.8V | 51.2 V
Critical AC load | Given | 6.0 kW
Blackout inverter efficiency | From curve at 88.8% load | 91.3931%
DC power from battery |  | 6.5650 kW
MAX DISCHARGE CURRENT |  | 128.22 A
Bank capacity | 5P × 330Ah | 1,650 Ah
Discharge C-rate |  | 0.0777 C | Very gentle
Bank rated max | 5P × 400A/unit | 2,000 A
Safety margin |  | 15.6× | Well within limits
B. Charging Currents (CORRECTED wording)
Parameter | Formula | Result | Notes
Peak PV DC power (both slopes) | From TMY weather simulation | 9.7973 kW
After CC efficiency (2×MPPT100-600) | × 0.95 | 9.3074 kW
MAX PV-DRIVEN CHARGING CURRENT |  | 181.79 A | CORRECTED: actual PV-driven peak
MPPT 100-600 rated max output | 2 × 100A rated | 200 A | Controller ceiling (not reached by PV)
Governing max charging current | min(PV-driven, CC rated) | 181.79 A | PV limits; CC not the bottleneck
Charge C-rate at 181.8A |  | 0.1102 C | Extremely safe
LFP max rated (≤1C) | 1 × 1650Ah | 1,650 A max | We use 11.0% of max
DISCHARGE: Max 128.2A is 0.077C on a 1,650Ah bank — 15.6× below the rated 2,000A. Reliable critical load supply with massive headroom. CHARGE: The two MPPT 100-600 controllers are each rated to 100A output (200A combined), but the actual PV production never drives charging above 182.4A at the 51.2V bus. The PV array — not the controller rating — is the governing limit. At 182.4A the C-rate is 0.110C, well within LFP safe-charge limits, preserving the full 2,500-cycle life rating.

## Q10 3-Year Simulation
Q10 – 3-Year Battery SoC Simulation ¦ Blackout timing: h>=20 Thu / h<4 Fri (20:00–04:00) ¦ Inverter losses included
A. Annual Summary
Parameter | Representative Year 1 | Representative Year 2 | Representative Year 3 | Notes
Nominal capacity (kWh) | 84.480 | 83.601 | 82.723 | 0.02% per cycle degradation
Degradation (%) | 0.000% | 1.040% | 2.080% | Cumulative from start of each year
Usable Interp A (80%×nom, kWh) | 67.584 | 66.881 | 66.178 | Floor=15% SoC
Usable Interp B (75%×nom, kWh) | 63.360 | 62.701 | 62.042 | Floor=20% SoC
DC demand per event (kWh) | 52.520 | 52.520 | 52.520 | 48 kWh AC ÷ 91.39%
Margin A (kWh) | 15.064 | 14.361 | 13.658
Margin B (kWh) | 10.840 | 10.181 | 9.522
Starting SoC (%) | 95.00% | 96.00% | 96.01% | Year 1 starts at 95%; Years 2 and 3 follow from the previous simulated end state.
End-of-year SoC (%) | 95.00% | 95.00% | 95.00% | Taken from the rolling hourly SoC simulation.
Actual min SoC during blackouts | 32.83% | 32.18% | 31.51% | Minimum SoC taken directly from the hourly SoC simulation.
ALL BLACKOUTS COVERED? | ✓ YES | ✓ YES | ✓ YES | Checked directly from hourly SoC values against the 20% SoC floor.
Annual GT yield (kWh) | 10380 | 10380 | 10380
B. Final SoC After 3 Years – Direct Q10 Answer
Parameter | Value |  | Unit | Notes
Total cycles | 52×3 = 156 representative cycles |  | cycles | Calculated from blackout mask: blackout hours ÷ 8 h/event.
Total degradation | 156×0.02% = 3.12% |  |  | Conservative: one blackout event is counted as one cycle.
Final nominal capacity | 81.844 |  | kWh
FINAL SoC AFTER 3 YEARS | 95.00% |  |  | End of Year 3 after recharge to the 95% SoC operating target
Final usable Interp A (80%) | 65.475 |  | kWh | >52.520 kWh needed ✓
Final usable Interp B (75%) | 61.383 |  | kWh | >52.520 kWh needed ✓
Final worst-case post-blackout SoC | 30.83% |  |  | Computed using final degraded capacity and simulated final SoC.
C. Monthly SoC Stats Year 1 (SoC %)
Month | Min SoC | Max SoC | Mean SoC | Notes
Jan | 32.83 | 95 | 82.21 | Post-blackout recharge visible
Feb | 32.83 | 95 | 85.03 | Post-blackout recharge visible
Mar | 32.83 | 95 | 87.15 | Post-blackout recharge visible
Apr | 32.83 | 95 | 88.36 | Post-blackout recharge visible
May | 32.83 | 95 | 88.75 | Post-blackout recharge visible
Jun | 32.83 | 95 | 89.89 | Post-blackout recharge visible
Jul | 32.83 | 95 | 88.49 | Post-blackout recharge visible
Aug | 32.83 | 95 | 88.98 | Post-blackout recharge visible
Sep | 32.83 | 95 | 88.15 | Post-blackout recharge visible
Oct | 32.83 | 95 | 85.99 | Post-blackout recharge visible
Nov | 32.83 | 95 | 84.17 | Post-blackout recharge visible
Dec | 32.83 | 95 | 82.63 | Post-blackout recharge visible

## Q11 LCA
Q11 – Life Cycle Assessment ¦ Tampa PV System ¦ Group 20
Grid carbon intensity used: 0.384 kg CO₂/kWh from the assignment-specified Our World in Data website
A. Embodied CO₂ by Component
Component | Quantity × Factor | CO₂ (kg) | Reference
AIKO 490W modules (24 units, 11.76 kWp) | 11.76×600 | 7056 | Frischknecht et al. 2015 – N-type mono ≈600 kg/kWp
Victron LFP 12.8V/330Ah (20 units, 84.48 kWh) | 84.48×75 | 6336 | Emilsson & Dahllöf 2019; Peters et al. 2017 – LFP 65–90 kg/kWh
XW Pro 6848 hybrid inverter (1 unit) | 1×150 | 150 | IEA-PVPS Task 12 (2015)
Conext MPPT 100-600 (2 units) | 2×30 | 60 | Proaño et al. 2017
Mounting structure (24 panels) | 24×15 | 360 | Alsema et al. 2006 – Al racking
DC/AC switchgear (2 units) | 2×20 | 40 | Industry average
Cables, racks, accessories | Lump | 80 | IEA-PVPS auxiliary
Monitoring system (1 unit) | 1×25 | 25 | Electronics estimate
TOTAL EMBODIED CO₂ | Sum | 14107 | kg CO₂eq — Global Warming Potential
B. Carbon Payback Time (CORRECTED note)
Parameter | Formula | Result | Notes
Grid carbon intensity from assignment website | Given | 0.384 kg CO₂/kWh | Our World in Data electricity carbon-intensity grapher
Annual AC yield used for payback | 10380 kWh | 10380 kWh | Grid-tied AC yield only; conservative basis consistent with Q2 savings calculation
Annual CO₂ savings |  | 3986.0 kg/yr
Total embodied CO₂ | Sum above | 14107.0 kg | 20-battery bank included
CARBON PAYBACK TIME |  | 3.54 years | Grid-tied-only payback basis
TOTAL GWP | 14107.0 kg CO₂eq | At system boundary | Embodied emissions
Net CO₂ benefit (25-yr) |  | 85542 kg CO₂ | Avoided over 25-year life

## Q1-Q3 Yield and Savings
Q1/Q2/Q3 – Yield, Grid-Tied Savings & Penalty Avoidance ¦ Tampa ¦ Load 3
Q1 – Annual AC Electricity Yield
Parameter | Value | Unit | Notes
Annual GT AC yield – Year 1 | 10380.0984 | kWh | Grid-tied only (SoC=95%)
Annual GT AC yield – Year 2 | 10380.0984 | kWh | Same TMY pattern
Annual GT AC yield – Year 3 | 10380.0984 | kWh
Annual backup delivered | 2496 | kWh | 52×8h×6kW – battery, not PV
Total AC produced Year 1 | 12876.0984 | kWh | GT + backup
Annual PV DC production | 15061.9 | kWh | Before CC losses
South slope POA | 1519 | kWh/m²
North slope POA | 1164 | kWh/m²
PR – grid-tied only | 0.658 | – | 10,400 ÷ (11.76×1,341) – low because PV also charges battery
PR – total AC production | 0.816 | – | 12,896 ÷ (11.76×1,341) – includes backup
Diffuse model note |  |  | Isotropic model used; Perez would add ~5–10% to yield
Monthly Grid-Tied Yield Breakdown Year 1
Month | GT AC (kWh) | Backup AC (kWh) | Notes
Jan | 440.1 | 240
Feb | 591.5 | 192
Mar | 859.2 | 192
Apr | 1159.8 | 192
May | 1285.9 | 240 | Peak GT months
Jun | 1244.3 | 192 | Peak GT months
Jul | 1207.9 | 222 | Peak GT months
Aug | 1069.6 | 210 | Peak GT months
Sep | 896.6 | 192
Oct | 757.6 | 240
Nov | 478.5 | 192
Dec | 389.2 | 192
TOTAL | 10380.1 | 2496
Q2 – Grid-Tied Savings Year 1
Parameter | Formula | Result | Notes
GT yield Year 1 | 10380.1 kWh | 10,400.3 kWh
Energy price | Table I | €0.24/kWh
ANNUAL SAVINGS – GT |  | €2491.22
Q3 – Total Savings Including Avoided Penalties Year 1
Parameter | Formula | Result | Notes
Clients | Given | 45
Compensation rate | Table I | €3.00/hr/client
Events/year | From blackout mask | 52
Hours/event | 20:00–04:00 | 8 h
Penalty without system |  | €56,160 | All avoided
Blackouts covered | ✓ YES | 52/52 | Zero penalties paid if all are covered
PENALTY SAVINGS |  | €56,160
GT energy savings (Q2) | Above | €2491.22
TOTAL ANNUAL SAVINGS |  | €58,651.22
3-year total | ×3 | €175,954 | Undiscounted

## Hourly Load Profile
Hourly Load Profile – Load 3 ¦ Tampa representative year ¦ First 168 hours shown (full year = 8,760 rows)
NOTE: The complete 8,760-hour profile was built in a separate file. Key parameters below.
Hour# | Month | DOY | Hour | Day-of-Week | Is Blackout? | Load (kW) | Active Load (kW) | Mode (sim)
1 | Jan | 1 | 1 | Wed | NO | 7.0075 | 7.0075 | IDLE
2 | Jan | 1 | 2 | Wed | NO | 7.0075 | 7.0075 | IDLE
3 | Jan | 1 | 3 | Wed | NO | 7.1362 | 7.1362 | IDLE
4 | Jan | 1 | 4 | Wed | NO | 7.2834 | 7.2834 | IDLE
5 | Jan | 1 | 5 | Wed | NO | 7.2834 | 7.2834 | IDLE
6 | Jan | 1 | 6 | Wed | NO | 7.4121 | 7.4121 | IDLE
7 | Jan | 1 | 7 | Wed | NO | 7.7064 | 7.7064 | IDLE
8 | Jan | 1 | 8 | Wed | NO | 7.7064 | 7.7064 | GRID_TIED
9 | Jan | 1 | 9 | Wed | NO | 7.9823 | 7.9823 | GRID_TIED
10 | Jan | 1 | 10 | Wed | NO | 7.9823 | 7.9823 | GRID_TIED
11 | Jan | 1 | 11 | Wed | NO | 8.111 | 8.111 | GRID_TIED
12 | Jan | 1 | 12 | Wed | NO | 8.111 | 8.111 | GRID_TIED
13 | Jan | 1 | 13 | Wed | NO | 8.2582 | 8.2582 | GRID_TIED
14 | Jan | 1 | 14 | Wed | NO | 8.2582 | 8.2582 | GRID_TIED
15 | Jan | 1 | 15 | Wed | NO | 8.111 | 8.111 | GRID_TIED
16 | Jan | 1 | 16 | Wed | NO | 8.111 | 8.111 | GRID_TIED
17 | Jan | 1 | 17 | Wed | NO | 7.9823 | 7.9823 | GRID_TIED
18 | Jan | 1 | 18 | Wed | NO | 7.9823 | 7.9823 | GRID_TIED
19 | Jan | 1 | 19 | Wed | NO | 7.8351 | 7.8351 | IDLE
20 | Jan | 1 | 20 | Wed | NO | 7.7064 | 7.7064 | IDLE
21 | Jan | 1 | 21 | Wed | NO | 7.5592 | 7.5592 | IDLE
22 | Jan | 1 | 22 | Wed | NO | 7.2834 | 7.2834 | IDLE
23 | Jan | 1 | 23 | Wed | NO | 7.1362 | 7.1362 | IDLE
24 | Jan | 1 | 24 | Wed | NO | 7.0075 | 7.0075 | IDLE
25 | Jan | 2 | 1 | Thu | NO | 7.0075 | 7.0075 | IDLE
26 | Jan | 2 | 2 | Thu | NO | 7.0075 | 7.0075 | IDLE
27 | Jan | 2 | 3 | Thu | NO | 7.1362 | 7.1362 | IDLE
28 | Jan | 2 | 4 | Thu | NO | 7.2834 | 7.2834 | IDLE
29 | Jan | 2 | 5 | Thu | NO | 7.2834 | 7.2834 | IDLE
30 | Jan | 2 | 6 | Thu | NO | 7.4121 | 7.4121 | IDLE
31 | Jan | 2 | 7 | Thu | NO | 7.7064 | 7.7064 | IDLE
32 | Jan | 2 | 8 | Thu | NO | 7.7064 | 7.7064 | GRID_TIED
33 | Jan | 2 | 9 | Thu | NO | 7.9823 | 7.9823 | GRID_TIED
34 | Jan | 2 | 10 | Thu | NO | 7.9823 | 7.9823 | GRID_TIED
35 | Jan | 2 | 11 | Thu | NO | 8.111 | 8.111 | GRID_TIED
36 | Jan | 2 | 12 | Thu | NO | 8.111 | 8.111 | GRID_TIED
37 | Jan | 2 | 13 | Thu | NO | 8.2582 | 8.2582 | GRID_TIED
38 | Jan | 2 | 14 | Thu | NO | 8.2582 | 8.2582 | GRID_TIED
39 | Jan | 2 | 15 | Thu | NO | 8.111 | 8.111 | GRID_TIED
40 | Jan | 2 | 16 | Thu | NO | 8.111 | 8.111 | GRID_TIED
41 | Jan | 2 | 17 | Thu | NO | 7.9823 | 7.9823 | GRID_TIED
42 | Jan | 2 | 18 | Thu | NO | 7.9823 | 7.9823 | GRID_TIED
43 | Jan | 2 | 19 | Thu | NO | 7.8351 | 7.8351 | IDLE
44 | Jan | 2 | 20 | Thu | YES | 7.7064 | 6 | BLACKOUT
45 | Jan | 2 | 21 | Thu | YES | 7.5592 | 6 | BLACKOUT
46 | Jan | 2 | 22 | Thu | YES | 7.2834 | 6 | BLACKOUT
47 | Jan | 2 | 23 | Thu | YES | 7.1362 | 6 | BLACKOUT
48 | Jan | 2 | 24 | Thu | YES | 7.0075 | 6 | BLACKOUT
49 | Jan | 3 | 1 | Fri | YES | 7.0075 | 6 | BLACKOUT
50 | Jan | 3 | 2 | Fri | YES | 7.0075 | 6 | BLACKOUT
51 | Jan | 3 | 3 | Fri | YES | 7.1362 | 6 | BLACKOUT
52 | Jan | 3 | 4 | Fri | NO | 7.2834 | 7.2834 | IDLE
53 | Jan | 3 | 5 | Fri | NO | 7.2834 | 7.2834 | IDLE
54 | Jan | 3 | 6 | Fri | NO | 7.4121 | 7.4121 | IDLE
55 | Jan | 3 | 7 | Fri | NO | 7.7064 | 7.7064 | IDLE
56 | Jan | 3 | 8 | Fri | NO | 7.7064 | 7.7064 | CHARGING
57 | Jan | 3 | 9 | Fri | NO | 7.9823 | 7.9823 | CHARGING
58 | Jan | 3 | 10 | Fri | NO | 7.9823 | 7.9823 | CHARGING
59 | Jan | 3 | 11 | Fri | NO | 8.111 | 8.111 | CHARGING
60 | Jan | 3 | 12 | Fri | NO | 8.111 | 8.111 | CHARGING
61 | Jan | 3 | 13 | Fri | NO | 8.2582 | 8.2582 | CHARGING
62 | Jan | 3 | 14 | Fri | NO | 8.2582 | 8.2582 | CHARGING
63 | Jan | 3 | 15 | Fri | NO | 8.111 | 8.111 | CHARGING
64 | Jan | 3 | 16 | Fri | NO | 8.111 | 8.111 | CHARGING
65 | Jan | 3 | 17 | Fri | NO | 7.9823 | 7.9823 | CHARGING
66 | Jan | 3 | 18 | Fri | NO | 7.9823 | 7.9823 | CHARGING
67 | Jan | 3 | 19 | Fri | NO | 7.8351 | 7.8351 | IDLE
68 | Jan | 3 | 20 | Fri | NO | 7.7064 | 7.7064 | IDLE
69 | Jan | 3 | 21 | Fri | NO | 7.5592 | 7.5592 | IDLE
70 | Jan | 3 | 22 | Fri | NO | 7.2834 | 7.2834 | IDLE
71 | Jan | 3 | 23 | Fri | NO | 7.1362 | 7.1362 | IDLE
72 | Jan | 3 | 24 | Fri | NO | 7.0075 | 7.0075 | IDLE
73 | Jan | 4 | 1 | Sat | NO | 7.0075 | 7.0075 | IDLE
74 | Jan | 4 | 2 | Sat | NO | 7.0075 | 7.0075 | IDLE
75 | Jan | 4 | 3 | Sat | NO | 7.1362 | 7.1362 | IDLE
76 | Jan | 4 | 4 | Sat | NO | 7.2834 | 7.2834 | IDLE
77 | Jan | 4 | 5 | Sat | NO | 7.2834 | 7.2834 | IDLE
78 | Jan | 4 | 6 | Sat | NO | 7.4121 | 7.4121 | IDLE
79 | Jan | 4 | 7 | Sat | NO | 7.7064 | 7.7064 | IDLE
80 | Jan | 4 | 8 | Sat | NO | 7.7064 | 7.7064 | CHARGING
81 | Jan | 4 | 9 | Sat | NO | 7.9823 | 7.9823 | CHARGING
82 | Jan | 4 | 10 | Sat | NO | 7.9823 | 7.9823 | CHARGING
83 | Jan | 4 | 11 | Sat | NO | 8.111 | 8.111 | CHARGING
84 | Jan | 4 | 12 | Sat | NO | 8.111 | 8.111 | CHARGING
85 | Jan | 4 | 13 | Sat | NO | 8.2582 | 8.2582 | CHARGING
86 | Jan | 4 | 14 | Sat | NO | 8.2582 | 8.2582 | CHARGING
87 | Jan | 4 | 15 | Sat | NO | 8.111 | 8.111 | CHARGING
88 | Jan | 4 | 16 | Sat | NO | 8.111 | 8.111 | CHARGING
89 | Jan | 4 | 17 | Sat | NO | 7.9823 | 7.9823 | CHARGING
90 | Jan | 4 | 18 | Sat | NO | 7.9823 | 7.9823 | CHARGING
91 | Jan | 4 | 19 | Sat | NO | 7.8351 | 7.8351 | IDLE
92 | Jan | 4 | 20 | Sat | NO | 7.7064 | 7.7064 | IDLE
93 | Jan | 4 | 21 | Sat | NO | 7.5592 | 7.5592 | IDLE
94 | Jan | 4 | 22 | Sat | NO | 7.2834 | 7.2834 | IDLE
95 | Jan | 4 | 23 | Sat | NO | 7.1362 | 7.1362 | IDLE
96 | Jan | 4 | 24 | Sat | NO | 7.0075 | 7.0075 | IDLE
97 | Jan | 5 | 1 | Sun | NO | 7.0075 | 7.0075 | IDLE
98 | Jan | 5 | 2 | Sun | NO | 7.0075 | 7.0075 | IDLE
99 | Jan | 5 | 3 | Sun | NO | 7.1362 | 7.1362 | IDLE
100 | Jan | 5 | 4 | Sun | NO | 7.2834 | 7.2834 | IDLE
101 | Jan | 5 | 5 | Sun | NO | 7.2834 | 7.2834 | IDLE
102 | Jan | 5 | 6 | Sun | NO | 7.4121 | 7.4121 | IDLE
103 | Jan | 5 | 7 | Sun | NO | 7.7064 | 7.7064 | IDLE
104 | Jan | 5 | 8 | Sun | NO | 7.7064 | 7.7064 | CHARGING
105 | Jan | 5 | 9 | Sun | NO | 7.9823 | 7.9823 | CHARGING
106 | Jan | 5 | 10 | Sun | NO | 7.9823 | 7.9823 | CHARGING
107 | Jan | 5 | 11 | Sun | NO | 8.111 | 8.111 | CHARGING
108 | Jan | 5 | 12 | Sun | NO | 8.111 | 8.111 | CHARGING
109 | Jan | 5 | 13 | Sun | NO | 8.2582 | 8.2582 | CHARGING
110 | Jan | 5 | 14 | Sun | NO | 8.2582 | 8.2582 | CHARGING
111 | Jan | 5 | 15 | Sun | NO | 8.111 | 8.111 | CHARGING
112 | Jan | 5 | 16 | Sun | NO | 8.111 | 8.111 | CHARGING
113 | Jan | 5 | 17 | Sun | NO | 7.9823 | 7.9823 | GRID_TIED
114 | Jan | 5 | 18 | Sun | NO | 7.9823 | 7.9823 | GRID_TIED
115 | Jan | 5 | 19 | Sun | NO | 7.8351 | 7.8351 | IDLE
116 | Jan | 5 | 20 | Sun | NO | 7.7064 | 7.7064 | IDLE
117 | Jan | 5 | 21 | Sun | NO | 7.5592 | 7.5592 | IDLE
118 | Jan | 5 | 22 | Sun | NO | 7.2834 | 7.2834 | IDLE
119 | Jan | 5 | 23 | Sun | NO | 7.1362 | 7.1362 | IDLE
120 | Jan | 5 | 24 | Sun | NO | 7.0075 | 7.0075 | IDLE
121 | Jan | 6 | 1 | Mon | NO | 7.0075 | 7.0075 | IDLE
122 | Jan | 6 | 2 | Mon | NO | 7.0075 | 7.0075 | IDLE
123 | Jan | 6 | 3 | Mon | NO | 7.1362 | 7.1362 | IDLE
124 | Jan | 6 | 4 | Mon | NO | 7.2834 | 7.2834 | IDLE
125 | Jan | 6 | 5 | Mon | NO | 7.2834 | 7.2834 | IDLE
126 | Jan | 6 | 6 | Mon | NO | 7.4121 | 7.4121 | IDLE
127 | Jan | 6 | 7 | Mon | NO | 7.7064 | 7.7064 | IDLE
128 | Jan | 6 | 8 | Mon | NO | 7.7064 | 7.7064 | GRID_TIED
129 | Jan | 6 | 9 | Mon | NO | 7.9823 | 7.9823 | GRID_TIED
130 | Jan | 6 | 10 | Mon | NO | 7.9823 | 7.9823 | GRID_TIED
131 | Jan | 6 | 11 | Mon | NO | 8.111 | 8.111 | GRID_TIED
132 | Jan | 6 | 12 | Mon | NO | 8.111 | 8.111 | GRID_TIED
133 | Jan | 6 | 13 | Mon | NO | 8.2582 | 8.2582 | GRID_TIED
134 | Jan | 6 | 14 | Mon | NO | 8.2582 | 8.2582 | GRID_TIED
135 | Jan | 6 | 15 | Mon | NO | 8.111 | 8.111 | GRID_TIED
136 | Jan | 6 | 16 | Mon | NO | 8.111 | 8.111 | GRID_TIED
137 | Jan | 6 | 17 | Mon | NO | 7.9823 | 7.9823 | GRID_TIED
138 | Jan | 6 | 18 | Mon | NO | 7.9823 | 7.9823 | GRID_TIED
139 | Jan | 6 | 19 | Mon | NO | 7.8351 | 7.8351 | IDLE
140 | Jan | 6 | 20 | Mon | NO | 7.7064 | 7.7064 | IDLE
141 | Jan | 6 | 21 | Mon | NO | 7.5592 | 7.5592 | IDLE
142 | Jan | 6 | 22 | Mon | NO | 7.2834 | 7.2834 | IDLE
143 | Jan | 6 | 23 | Mon | NO | 7.1362 | 7.1362 | IDLE
144 | Jan | 6 | 24 | Mon | NO | 7.0075 | 7.0075 | IDLE
145 | Jan | 7 | 1 | Tue | NO | 7.0075 | 7.0075 | IDLE
146 | Jan | 7 | 2 | Tue | NO | 7.0075 | 7.0075 | IDLE
147 | Jan | 7 | 3 | Tue | NO | 7.1362 | 7.1362 | IDLE
148 | Jan | 7 | 4 | Tue | NO | 7.2834 | 7.2834 | IDLE
149 | Jan | 7 | 5 | Tue | NO | 7.2834 | 7.2834 | IDLE
150 | Jan | 7 | 6 | Tue | NO | 7.4121 | 7.4121 | IDLE
151 | Jan | 7 | 7 | Tue | NO | 7.7064 | 7.7064 | IDLE
152 | Jan | 7 | 8 | Tue | NO | 7.7064 | 7.7064 | GRID_TIED
153 | Jan | 7 | 9 | Tue | NO | 7.9823 | 7.9823 | GRID_TIED
154 | Jan | 7 | 10 | Tue | NO | 7.9823 | 7.9823 | GRID_TIED
155 | Jan | 7 | 11 | Tue | NO | 8.111 | 8.111 | GRID_TIED
156 | Jan | 7 | 12 | Tue | NO | 8.111 | 8.111 | GRID_TIED
157 | Jan | 7 | 13 | Tue | NO | 8.2582 | 8.2582 | GRID_TIED
158 | Jan | 7 | 14 | Tue | NO | 8.2582 | 8.2582 | GRID_TIED
159 | Jan | 7 | 15 | Tue | NO | 8.111 | 8.111 | GRID_TIED
160 | Jan | 7 | 16 | Tue | NO | 8.111 | 8.111 | GRID_TIED
161 | Jan | 7 | 17 | Tue | NO | 7.9823 | 7.9823 | GRID_TIED
162 | Jan | 7 | 18 | Tue | NO | 7.9823 | 7.9823 | GRID_TIED
163 | Jan | 7 | 19 | Tue | NO | 7.8351 | 7.8351 | IDLE
164 | Jan | 7 | 20 | Tue | NO | 7.7064 | 7.7064 | IDLE
165 | Jan | 7 | 21 | Tue | NO | 7.5592 | 7.5592 | IDLE
166 | Jan | 7 | 22 | Tue | NO | 7.2834 | 7.2834 | IDLE
167 | Jan | 7 | 23 | Tue | NO | 7.1362 | 7.1362 | IDLE
168 | Jan | 7 | 24 | Tue | NO | 7.0075 | 7.0075 | IDLE
Annual Simulation Summary (full 8,760 hours)
Total hours | 8,760
Blackout hours | 416 (52 events × 8h)
Grid-tied hours | 3355
Charging hours | 1048
Idle hours | 3941
Annual GT AC yield | 10380.1 kWh
Annual backup delivered | 2496.0 kWh
Min SoC during blackouts | 32.83%
Final SoC end of Representative Year 1 | 95.00%